## Table 1
Question Number | Drawing Sheet Number | Specification Number | Question | Response
1 | C210, C305 |  | C210 calls for 16" diameter piers, C305 calls for 18" diameter piers. Please confirm required diameter of these piers. | Sheet 210 has been removed from Bid Set. Pier diameters shown on C305 are correct.
2 | C210, C305 |  | Wall thickness on C210 calls out 10", thickness on C305 calls out 12". Please confirm required wall thickness. | Sheet 210 has been removed from Bid Set. Wall thickness shown on C305 are correct.
3 | C103, C104 |  | C103 calls for 4"asphalt over 6" base course. C104 section calls for 4" asphalt over 12" base course. Please confirm what is required. | Sheet C104 now includes additional typical pavement section. Parking lot pavement section is 4-inches asphalt over 6" of base course. Patch back within public or private right-of-way is 4-inches of asphalt over 12-inches of base course.
4 | A102 |  | Will any areas indicated as "Exposed to Structure" require field applied paint? | Field paint all exposed structure. General note added to A611.
5 |  | 099600 | High Performance paint specification 3.4/A schedules an Epoxy Non-Slip Deck Coating system for Horizontal Concrete substrates. Where does this coating occur? Please clearly define conditions that are to receive high performance paint. | Reference Sheet A101 Overall Floor Plan. Concrete floor areas designated with diagonal hatch pattern on the Overall Floor Plan and all raised concrete curb areas (islands) in Bus Parking 100 shall receive an Epoxy Non-Slip Deck Coating system for Horizontal Concrete Substrates.
6 |  | 099600 | High Performance paint specification 3.5/D schedules epoxy modified latex at Gypsum board substrates. Interior Painting specification 09 91 23 3.4/G schedules latex over latex sealer system. What conditions require the epoxy modified latex? | All exposed gypsum board wall finishes in Bus Parking 100 shall receive epoxy modified latex High Performance finish. All other interior gypsum board wall finish shall be latex over latex sealer system.
7 | A601 |  | General Note#1 states "All door frames to be painted". Shall we assume paint at all interior and exterior hollow metal doors as well? What type of specified paint is required at hollow metal doors and door frames? | Reference specifications section 099123 Interior Painting. All interior and exterior hollow metal doors and frames shall be painted per 099123/3.4, D.1 Latex System, Alkyd Primer.
8 | A601 |  | The door schedule on A-601 shows multiple wood doors, but no specification for wood doors is provided. Please provide a specification, and advise if the doors are to be solid core, be prefinished, etc. | Specification Section 081416 Flush Wood Doors added.
9 | A601 |  | Are all window types shown on A601 aluminum windows? | All window types shown on Sheet A601 are aluminum windows.
10 | A611 |  | The finish schedule shows some rooms are to receive porcelain tile flooring. There is no spec for porcelain tile, only ceramic tile. Please provide specifications for porcelain tile. | Specification Section 093013 updated to include porcelain tile flooring.
11 | A502 |  | Architectural details shown on sheet A502 show dampproofing at building foundation. Bid documents only include a specification for Cold Fluid Applied Waterproofing. Please clarify if we are to waterproof or dampproof building foundations and if applicable, please provide a specification for dampproofing. | The Administration Building portion of the building bears on shallow foundations with the walls above grade. At the Bus Storage building, considerable portions of the exterior walls are retaining walls below grade. At shallow foundations with walls above grade, dampproofing of the foundation walls is acceptable. At locations where the exterior walls are retaining walls, fluid applied waterproofing shall be applied. Section 071113 Bituminous Dampproofing has been added.
12 | C203, C204 |  | Please advise what pavement thickness is required for the private road and transit drive. | Pavement sections for Private and Public Roads are noted on Sheets C202, C203 and C204. Minimum pavement section is 4-inches of asphalt on 12-inches of base course. Refer to C104 for typical section.
13 | C307, C308, C309, C310 |  | Please verify if scales on civil drawings are correct. When scaling various dimensional callouts, it appears the scale on the civil drawings should be a 1" = 30' scale, not a 1" = 40' scale. | Scale is 1"=30'. Revised scale bar provided.
14 |  |  | Has the Owner submitted an application for the design, delivery & installation of the primary electrical transformer? When is the transformer scheduled to arrive/install? | Yes (Load Data Form). Contractor to coordinate with CSU.
15 |  |  | Please provide structural details for the steel angle at the overhead door jambs/head conditions. | The overhead door structure shall be part of the PEMB.
16 |  |  | Please provide structural detail for support of the overhead door operators. Typically this is a 1/4" steel plate that the operator mounts to as the standard PEMB supports will not adequately carry the load of the operators. | GC to coordinate with PEMB manufacturer to provide necessary support for the door operators.
17 |  |  | Will interior steel columns require paint above concrete wraps (42" and above)? If so, what type of specified paint? | Yes. All exposed structure to be field painted.
18 | FS111 |  | Per note FP9, fire sprinklers will not be provided for the administrative part of the building. Please confirm this is acceptable, per code, and that the GC should not provide any fire protection for the administrative portion. | The Administrative part of the building is separated from the parking garage area by 2-hr fire resistance rated fire barriers. The parking garage area and admin area are considered separated occupancies. The Adminstrative part of the building is its own fire area. The IBC/IFC do not require sprinkler protection to be provided for single -story Group B fire areas. The current design is acceptable per code. Refer to Architectural plan A-100 for building code information. - BCER
19 | A611 |  | Room finish schedule indicates Polished Concrete at Storage, Electrical, IT, Janitor rooms. It is atypical to have a polished concrete finish at these room types. Is the finish schedule accurate for these locations? | The finish schedule has been clarified as follows: Floor finish in Storage, Electrical, IT, and Janitor room may be Sealed Concrete in lieu of polished concrete.
20 | A611 |  | General Note#3 states that all polished concrete to be included in phase 1. Is the polished concrete in the administration area not to be part of alternate#1? Please clarify. | Sheet A611 General Note 3 has been modified to include concrete polishing in Alternate 1. Reference specification section 012300 ALTERNATES, 3.1 Schedule of Alternates for Base Bid and Alternate scope.
21 | E211A |  | Keynote E11 states, "Vehicle detector loop. Provide two loops of conductors in detector loop of type XLEP or RHW#12 CU in 2" SCH 40 PVC in a 30'X15' Space…See Vendor drawings for additional requirements". Vendor drawings cannot be found, and product information cannot be located in Electrical Specifications. Please provide further information for Vehicle detector loop requirements. | See sheet E211A for additional information.
22 |  |  | Please provide the most recent wage determination sheet for this project. | Please see Addendum 2 Form, questions 6 and 9.
23 |  |  | Please confirm that all DBE Enclosure Forms need to be submitted with the proposal on bid day. | Please see Addendum 2 Form, question 18.
24 |  |  | Can Enclosure 1B be separated from the other Enclosures so that the Subs can fill this form out on their own? | Yes, as long as it is returned with the proposal, notarized.
25 |  |  | Who is responsible for Builder’s Risk (Owner or GC)? If by Owner, please provide a copy of the policy. | The Prime Contractor is responsible for all facets of the insurance requirements.
26 |  |  | Is the low-voltage scope of work limited to the pre-approved contractor (Linx) or may other contractors bid the work so long as they meet the experience criteria for this type of project? | Other contractors are able to place bids, however, qualifications must be met per Specification 27 00 20 requirements to be considered. Linx has been listed as preselected under telecom due to meeting these qualifications already
27 |  |  | Can Varco Pruden be approved as a Metal Building supplier? | Yes. Per 113419: "Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to the following:..." A&S, Butler, VP, Chief and others are acceptable.
28 |  |  | Can Chief Buildings, INC. (out of Grand Island, NE) https://chiefbuildings.com/ be approved as Metal Building supplier? (a) If yes, can the Chief MVP 24ga Roof Panel (or similar) be substituted for the Berridge Zee Panel? | Yes. Per 113419: "Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to the following:..." A&S, Butler, VP, Chief and others are acceptable.
29 |  |  | Can the Metal Sales TLC-2 (or similar) be substituted for the Berridge Vee Panel? | Yes, Berridge is the "Basis of Design" but other manufactures meeting the performance of the specifications may be used.
30 |  |  | Bid documents note that the period of performance is 365 days from issuance of the Notice to Proceed. Currently, the Notice to Proceed date is denoted as “TBD”. What date shall bidders assume for issuance of an NTP? | May 1, 2021
31 |  |  | What is the assumed Notice to Proceed Date (for scheduling and procurement of the pre-engineered metal building)? | May 1, 2021
32 |  |  | Bid documents note that liquidated damages at a rate of $1500/per day (projects over $1,000,000) are applicable. Do liquidated damages apply if substantial completion is achieved within the 365 day period of performance, or does final completion need to be achieved within the 365 day period of performance? | Final completion must be achieved within the 365-day performance period. Following the 365-day performance period, Liquidated Damages will be assessed daily until final completion is achieved. (Also - please see Addendum 2 Form, question 12.)
33 |  |  | How will substantial completion be defined? | Substantial completion is the stage when the project is sufficiently completed so that the City can use it for its intended purpose. This includes, but is not limited to, transit buses being parked in and operating daily from the facility, a certificate of occupancy has been granted for the bus storage building and the administration spaces (if Add Alt is awarded), outside parking is available for staff use, the detention pond and rundown are functional, and all site safety features are completed.
34 |  |  | On the bid form, shall GCs include all costs related to General Conditions, General Requirements, Insurance, Bonds, etc. with the Division 1 – General Requirement Costs? | How that cost is broken out is on the Vendor, as long as during negotiations it can be discussed
35 |  |  | What thickness of asphalt shall be assumed for the unit price information? | Refer to Section 012200, Part 3, 3.1(C) and (D). Removal of asphalt paving is assumed to be 4-inches for roadways and within property boundaries. Part 3, 3.1(D) has been revised to provide further clarification.
36 |  |  | re: Section V - 107.26 – Testing of Materials. Paragraph states that the City will contract with a 3rd party for testing related to Soil Compaction, Cast-in-Place Concrete & Asphalt Concrete Pavement, but that Contractor is responsible for testing & associated fees of all other testing and inspections required by Contract Documents. Please provide a matrix of all other tests/inspections that the City expects will be required on this project so that all GCs are pricing the same scope(s). | The City will contract with a 3rd party for the purpose of Quality Assurance (or Verification) testing for: Soil Compaction Control; Cast-in-Place Concrete; and Asphalt Concrete Pavement. The Contractor is responsible for the performance and associated costs for all other tests and inspections required by the contract documents and for any Quality Control testing that the Contractor deems necessary to ensure conformance of proposed materials and installation with project requirements.
37 |  |  | What is the BID depth/length for Drilled Piers (other than 6’ penetration into un-weathered Bed Rock)? | Bed rock is expected at a depth of 20-40 feet per the soils report, with significant variation across the site. A bid depth of 45 feet should be used.
38 |  | 284621 | Per Specification 284621.11 section 2.1.A, it states the following: “Manufacturers: Subject to compliance with requirements, provide products by one of the following: 1. Fire Alarm Control Unit: a. Johnson Controls – Simplex Grinnell” (a) Are other equivalent manufacturers permitted? If so, which list of equivalent manufacturers are permitted? (b) Would Edwards EST panel be acceptable as they meet all other requirements of this specification section. | Equipment by other manufactures will be considered an "approved equal" and accepted, provided it fully meets the requirements of the specifications although Simplex is the preferred manufacturer of the Owner. *Please note: A full fire alarm system is not being provided for the building. This was removed prior to the CD deliverable. The only fire alarm requirements for the building include a control unit to monitor the sprinkler system, a dialer, a smoke detector adjacent to the control unit, and a horn/strobe above the FDC.
39 | C001, C201 |  | re: Contract Documents. The title on the index does not match the .pdf file as it pertains to C201 REMOVALS and C001 REMOVALS. Please revise. | As the City requires individual approvals for each civil construction plan set with separate approval stamps, this construction document plan set will have three identical Removal Plans. C201, C301 and C401.
40 | A004 |  | re: Contract Documents. Sheet A004 COMCHECK appears as a .pdf file but does not appear on the index. Please confirm this sheet was intended to be issued. | A004 was removed as a sheet from the drawing set in response to a PPRBD comment and provided in 8.5/11 format. The information is still applicable.
41 |  | 034500, 230993 | re: Project Specifications. The Table of Contents lists 034500 Precast Architectural Concrete and 230993.11 Sequence of Operations of HVAC DDC. The sections do not appear to be included. Please provide these sections. | 034500 has been added. 230993.11 is not used.
42 |  | 230923, 323143 | re: Project Specifications. Spec sections 230923 Direct Digital Control (DDC) System for HVAC and 323143 Automatic Steel Gate are provided, but not listed on the Table of Contents. Please confirm these sections are applicable to this project. | 230923 and 323143 added to Table of Contents.
43 |  |  | Please confirm that the Ashford Formula is to be put down in the large Bus Parking Area. This is typically put down within two (2) days after the slab is poured so it would be done at a separate time from the Polished Concrete areas to allow for the 28 days for the slab to fully cure before we can polish. | The bus parking area is not polished concrete rather sealed concrete.
44 |  |  | Would the Owner consider changing the floor finish in corridor (131A) from sealed concrete to polished concrete? It is somewhat atypical that the corridors would not receive a polished finish when several of the rooms are received a polished finish. The transition between an 800-grit polish with a high shine and a sealed concrete with a matte finish will likely be noticeable and may not be what the design team expects. | The Corridor has been updated to Polished Concrete.
45 |  |  | Is it intended that the Janitor, IT, Storage and Electrical Rooms are to receive a polished concrete finish? Typically, these room types would receive a sealed concrete finish which is more economical. | Sealed Concrete is acceptable at Storage, Electrical, IT, and Janitor Rooms.
46 |  |  | At the copy room, there is no wall deVIDing the corridor and per the finish schedule, we have polished concrete in the copy room with sealed concrete in the corridor. What/how is the transition between these finishes to look like? | The Corridor has been updated to Polished Concrete.
47 |  |  | re: Access Control. Will the owner accept S2 as a manufacturer for software and head end equipment? | The access control system will be managed by the City which currently uses Software House Ccure 9000. No substitutions are permitted.
48 |  |  | Documents do not appear to note where window coverings are required. Shall we assume all windows in the Admin Area are to received window coverings? Are window coverings all to be part of the Add-Alternate? | Yes. All windows in the Admin Area are to receive window coverings. Window coverings are to be part of the Admin Alternate.
49 |  | 122413 | re: Spec Section - 122413 Roller Shades: (a) 1.1 A 1 asks for Manual Shades and 1.2 B asks for motorized shades. Please clarify whether or not these apply to this project. (b) 2.2 G has all the options for shades. Please verify fascia, headbox or recessed pocket install is applicable. (c) 2.4 C 2 mentions Skylights – I did not see any in the plans. Please clarify whether or not these apply to this project. (d) 3.1 A 1 asks for Opaque (which is blackout) but 2.1 F 1 says light filtering. Please confirm which is correct. If light filtering is required, what openness shall we price? (e) 3.1 B references motorized components. Is this applicable to this project? | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
50 | A011 |  | re: Detail(s) X1& X2, Sheet A-011. Details show gypsum board attaching directly to the wall girts. Due to how much these girts tend to sag, direct attachment is not advised by several drywall contractors as it leads to cracking. Typically, these walls are furred out with 1-5/8” or 2-1/2” steel stud or 7/8” hat channel. Should pricing represent what is drawn or does the design team wish to revise this assembly? | Fur out these walls with 7/8" hat channel. Sheet A011, details X1 and X2 will be revised.
51 |  |  | Please confirm Collateral load for Metal Buildings structure. | The preliminary metal building design uses a collateral load of 10 psf
52 | A311, A312 |  | Please confirm that metal building does not support any of the retaining walls: A311-5, A312-3&4. | The metal building does not provide structural support to the retaining walls
53 |  | 074213 | Confirm exterior wall panel is to be used as the interior liner panel as called out in Spec 07 42 13 1.1-A | Reference to metal liner panels in 1.1.1 has been deleted.
54 |  |  | Clarify wall insulation value: Drawings call out for R30 batt, specs call for R21 batt | Reference specification section 072100 Thermal Insulation, paragraph 2.2. Note that an R-value is not indicated for Glass-Fiber Blanket Insulation. Reference the drawings for required R-value. Reference paragraph 2.3 Glass-Fiber Board Insulation. Note that an R-value is not indicated for Glass-Fiber Board Insulation. Reference the drawings for required R-value. The reference to Thermal Resistivity (which is not the R-value) has been deleted from 2.3.B and 2.3.C. The 2015 Energy Conservation Code for Climate Zone 5 requires the following for metal buildings: Roofs: R-19 + R11 LS (per ASHRAE 90.1), Walls Above Grade: R13 + 13ci., and Walls Below Grade R-7.5ci. Alternatively provide R-30 wall insulation and achieve a U-Factor of 0.052 as shown on the drawings.
55 |  |  | Confirm metal building supplier is to determine roof insulation thickness to meet U-value on A011 R1 roof assembly. | Confirmed. The 2015 Energy Conservation Code for Climate Zone 5 requires the following for metal buildings: Roofs (metal building): U-0.035.
56 | A011 |  | Please provide more information/specifications/product on Metal Panel called out on bottom of purlin on A011- R1 Roof assembly. | Provide standard metal 29ga min. ceiling liner panel by PEMB manuf. Or equal.
57 | A111, A401 |  | Please coordinate the ramp and stairs at Driver Dispatch 111A with the structural sheets. | Structural has added a note to reference Architectural details
58 |  |  | Please confirm the intent is to run the gas lines above the roof. If yes, please provide a detail that shows gas line support to the standing seam roof. | Natural gas piping to be routed on roof. Pipe support on roof detail provided on MP301.
59 | C309 |  | Please coordinate the 12'-0" x 6" reinforced grass pavement maintenance access road with the Landscape drawings. | Note added to Landscape Plan.
60 |  |  | Please provide a product specification for the reinforced grass pavement access maintenance road. | Provide Presto GeoSystems 1.2" PE GeoBlock with 6" base. Install per manufacturer's recommendation and seed with specified mix.
61 |  |  | Are GCs permitted to provide qualifications and/or clarifications of their pricing with the bid proposal? | Yes.
62 | A611 |  | Will paint be required at the entirety of the CMU wall that demises (divides) Administration Area from Bus Parking as part of Alternate 1? Will the side of the CMU wall that is facing Bus Parking require paint, as part of the base bid? | The CMU wall that separates the Administration area from Bus Parking shall be painted from floor to 4" above the suspended ceiling. The wall shall be painted full height on the Bus Parking side with 2-part epoxy paint.
63 | A111 |  | Will the 8" tall concrete islands shown in Bus parking area require paint or a concrete sealer? | The raised concrete islands in Bus Parking area shall be painted.
64 | A501 |  | re: topping in room 111A Dispatch. Ramp just shows plywood over insulation and we are wondering if this is all that is required in the room versus the detail on A501 that appears to show concrete topping. | Detail on A401 revised to show 2" topping slab. Detail 8/A501 has been removed.
65 |  |  | Can the AISC certification on the steel fabrication be waived? There is such a small quantity of steel, that many of the AISC certified fabricators are not interested in pricing this project. | The AISC certification requirment may be waived as requested.
66 |  |  | Regarding Data/Low Volt: Please confirm Structured cabling contractor will not be responsible for any wireways, conduit or cable tray and that will be provided by the electrician. | Yes. As noted in the Communications Responsibility Matrix on sheet T003, these are to be provided by the electical contractor.
67 | T051 |  | Regarding Data/Low Volt: Handhole on note T38 on Sheet T-51 is assumed as provided by electrician also, please confirm this is not something that we need to carry. | As noted in the Communications Responsibility Matrix on sheet T003, these are to be provided by the electical contractor.
68 | T111 |  | Regarding Data/Low Volt: For WAPs noted as T36 on sheet T111, Please confirm cable only scope with jacks on both ends. | Per note T36 ALL rough-in to include conduit, cable, connectors, and J-box will be provided. Cable and connectors shall be installed for future WAPs.
69 |  |  | Regarding Data/Low Volt: Please provide required cable types for any speakers, AV, or security cables noted if not clearly called out in spec book. | Reference Equipment Schedules per each dicipline on the drawings and specs for cable details.
70 |  |  | Regarding Data/Low Volt: Please confirm whether or not Structured cabling contractor will be responsible for providing all IDF and MDF equipment, Racks, cable tray, and cable management, or if owner will provide. | Yes. As noted in the Communications Responsibility Matrix on sheet T003, these are to be provided by the Telecommunications contractor. See Equipment Schedules on Sheet T005 for specified equipment.
71 |  |  | Regarding Data/Low Volt: Please provide specs on equipment mentioned in previous RFI if not clearly called out in specifications.- Will the OSP cabling from 1015 Transit Dr. be a home run between buildings or F22will the communications contractor be responsible for splicing onto existing cabling? | This is detailed in Sheet T511. OSP fiber is to be provided by Telecommunications contractor and ran from the existing MDF in 1015 Transit Drive to TR-1 at new location. As noted, an existing handhole accross the street (west) of 1015 Transit Dr shall be used for this cabling. No fiber cabling is to be spliced.
72 |  |  | Is there an estimated footage from the new facility to 1015 Transit Dr. for OSP fiber optic cable length? No footage given on the drawing. | This will need to be determined in the field for exact distance before installation. Estimated pathway distance is 1,300 feet.
73 | T051, T401 |  | Drawing T051 shows the OSP cabling from 1015 Transit Dr. entering the facility in TR-1, Drawing T401, Detail 2, shows the OSP fiber in R-1 in MDF-1, Drawing T511 Backbone Cable Schedule shows the OSP cabling entering TR-1 and on the same drawing, Detail 1 shows the OSP cable entering in MDF-1. Where is the OSP Cable from 1015 Transit Dr. supposed to enter the facility? | OSP cable shall enter into and terminate in TR-1. OSP fiber from 1015 Transit Drive shall enter and terminate in TR-1.
74 |  |  | The Responsibility Matrix calls for the Telecommunications Contractor to provide network cabling and patch cords for the PA system, however the drawings do not indicate any network cabling to be installed for the PA. Is there category 6 network cabling that is required to be installed for the PA system and are there patch cords needed for the PA? | Patch cords will be required to connect PA to network/phones as shown on T504.
75 |  |  | What is the floor tile spec for the restrooms, same as the walls? What is the Cpt2 spec? | Spec 093013 has been updated to include porcelain floor tile.
76 |  |  | Will there be separate plans specific to the metal building? | A fully engineered plan set is to the PEMB manufacturer.
77 | S001 |  | Inspections – please clarify if the GC is responsible for the special inspections on S001. Please also clarify if GC is responsible for relevant third-party inspections such as asphalt testing. | The special inspections shall be performed by qualified third party individuals contracted by the GC.
78 |  |  | Should the office build out alternate be priced to be constructed concurrently with the bus parking building or should we assume a second mobilization and associated general conditions costs to come back and complete the office build out after the main bus parking building has been completed? | Concurrently with bus storage/parking construction (i.e. only one mobilization, but Add Alt can include pricing/elements of Mobilization that may only be required for Admin construction).
79 |  |  | Should drywall and finishing on the inside of the exterior walls in the office area be included in the base bid or in the alternate? | Included in Add Alt.
80 |  |  | Is the GC responsible for permitting fees? | Yes
81 |  |  | Is the GC responsible for plan review fees? | Already paid by MMT.
82 |  |  | Is the GC responsible for including costs for Builder’s risk and General liability insurance? | The Prime Contractor is responsible for all facets of the insurance requirements.
83 |  |  | After visiting the site, it was observed that water valves, water lines, wastewater manholes, and sewer cleanouts are around the existing vac truck cleanout and near the weigh scale foundation. These items are not on the “removals” sheet or the utility drawings. Will additional demolition/utility drawings be issued to clarify what should be done with these items? | All components for related to vac truck and weigh scale improvements shall be removed in their entirety to facilitate construction. Contractor shall remove sanitary or water systems to mainlines and cap in accordance with Colorado Springs Utility requirements. Respective Removal Plans have been updated to reflect this directive.
84 |  |  | After visiting the site, it was observed that there is a dumpster onsite, please clarify what should be done with that. | City to remove prior to construction activity.
85 |  |  | After visiting the site, it was observed that there is more existing asphalt than the current “removals” drawings depict. Will additional demolition drawings be issued to clarify what asphalt should be removed? | No additional demolition drawings will be issued. The contractor shall remove all asphalt as depicted and as necessary to facilitate construction in accordance with construction documents. The contractor may also refer to the Geotech Report provided in Volume 2 of the Project Manual for further information and interpretation of limits of asphalt.
86 | C105, C106,C107, L101, A050 |  | Sheet A050, L101, C105, C106,C107 show chainlink fencing. The building elevations show decorative fencing. Can a drawing be provided that clearly shows what fencing shall be decorative and what fencing shall be chainlink? | Chainlink and decorative fence is noted by linetype on respective Civil Sheets. More particularly, the chainlink fence is along the west, south and east property boundaries to the south and east entrance. Decorative fence is from the southeast entrance along the east and north boundary lines.
87 | A101, A202 |  | Sheet A101 has two detail call outs to details 3 and 4 on A202. Can you please provide sheet A202? | Sheet A202 has been renumbered to A 313 and added to the drawing set.
88 |  |  | Can a spec section for corner guards be provided? | Cornergaurds have been added to spec section 092900 - Gypsum Board. Provide 1 1/2" x 1 1/2" x 4' SS cornerguards at all interior corners of gypsum board walls.
89 | A111, A401, A501 |  | General note 2/A111 notes a raised floor in Driver Dispatch 111A. Detail 8/A501 shows the floor being a combination of structural foam and a slab. What is the thickness of the topping slab? Is reinforcing required? Can a spec section be provided for the structural foam? What should the perimeter walls in this room be to allow for foam and concrete? Detail 2/A401 eludes to the floor having plywood underlayment, is this needed? | See updated detail 3/A401 and new details 5&6/A401. Detail 8/A501 has been removed.
90 |  |  | Will the owner be providing and installing TV’s? If not, can a spec section be provided? | All AV equipment is to be provided by contractor. All equipment is shown on drawings. Refrence sheets T501-T504.
91 | A101, A111 |  | Sheet A101 and A111 have keynotes 5.36 and 5.37 for 6” and 12” bollards and both sheets show a lot of circles that I assume represent bollards. Can revised drawings be provided that call out which and where bollards are to be located so that accurate counts and sizes can be located? | Fill for steel column has been updated to solid grey to help differentiate between column wrap and bollards.
92 | A101, A111 |  | a. Keynote 3.39 indicates a steel column that should be encased in concrete, this can be easily confused with the other circles representing bollards. Can a revised drawing be provided to clarify what columns should have this encasement? | Fill for steel column has been updated to solid grey to help differentiate between column and bollards.
93 |  |  | Keynote 9.37 calls for “lane and walkway paint” there are only two callouts for lane/parking/walkway paint. Is this correct, can a revised drawing be issued that shows all interior line painting? | Walkway paint is denoted by diagonal hatch. Additional keynotes have also been added.
94 |  |  | Keynote 5.39 calls for premanufactured canopies. Can details that show the sizes of the canopies be provided as well as a spec section? | Dimensions have been added to A114. Provide Kawneer Versoleil Sunshade System or similar.
95 |  | 133419 | Spec Section 13 34 19 2.5 calls for fiber cement siding and soffits. I couldn’t find this on the drawings. Where should fiber cement siding and soffits be used? | Reference to Fiber Cement Siding and Soffit has been deleted from specification section 133419.
96 | A423 |  | Does the 6” concrete base called out on A423 require any reinforcing or doweling into the floor slab? | No or at contractor's discretion.
97 |  |  | Can a spec be provided for the car stops? | Wheel stop detail has been provided on Sheet C105.
98 |  |  | Can details/specs be provided for the ADA parking signage? | Sheet C103 has been updated with MUTCD code and size.. Detail is found on Sheet C104
99 | A423 |  | Sheet A423 shows a half wall, can the wall type and height be specified? | Wall to be Type A1 and height 3'-4"
100 |  |  | Can a detail be provided to show the PLAM cap on the half wall at the driver dispatch? | PLAM cap changed to wood cap. Reference Details 5 & 6/A401 for low wall details, including wood cap
101 | A423, A501 |  | 12/A501 shows a wood trim at the head of this window.9/A423 appears to show this same wood. Can a drawing be provided to show which windows ( heads, jambs, sills) are to receive this wood trim? Can a spec be provide that calls out the species of wood and what type of finish it is to receive? | The wood trim has been removed.
102 |  |  | The door schedule calls out opening 109A and 109B including the sidelights to be 11’8”. The floor plan shows these frames at 9’3 and 9’9. Please specify which is correct. | For both doors 109A and 109B, the opening for the doors shall be 6'-0" wide. The overall width of door plus sidelights shall be 9'-3" (for both doors).
103 |  |  | Please provide an elevation view of window FF and specifications, located between rooms 111A/111B | Reference Interior Elevation 10/A423 for elevation view of window FF. This is an interior aluminum horizontal sliding window with 1/2" tempered plate glass similar in style and by same manuf. as all other windows.
104 |  |  | Please provide a specification section for transaction windows "EE" and "FF" | Reference detail 8/A601 for a representative 3-D view of the EE window. Provide a 12" Stainless Steel Counter under the entire length of each EE window with a 12" wide drop-in deal tray in each. Windows "EE" and "FF" should be similare in stle and by same manuf. as all other windows.
105 |  |  | Please provide the location of the storefront detail 7/A501. Is this location at door 109A? | Storefront detail 7/A501 references Door 109A.
106 | A004 |  | Please provide current updated overall U values required for all storefront doors per sheet A004. | 2015 Energy Conservation Code (ECC) requires minimum U factors of 0.38 for fixed fenestration and 0.77 for entrance doors.
107 |  | 084113, 085113 | Please define the sample color of the 2 coat paint finish required in Section 084113.2.8.A. and 085113.2.5.A or are we to provide custom color paint allowance? | Provide a custom color paint allowance.
108 |  | 085113 | Regarding section 085113 Aluminum windows | Responses below.
109 |  | 085113 | a. page 2. section 2.1 These references do not apply to storefront. Are windows "AA, BB, CC, and DD" storefront windows? | Contractor's option to supply Windows as storefront by the same manufacturer as the other storefront assemblies.
110 |  | 085113 | b. Storefront is not available with AAMA labels or CW 30 ratings | AAMA labels and CW 30 ratings may be omitted.
111 |  | 085113 | c. Or are these references to window "EE"? | AAMA labels and CW 30 ratings may be omitted.
112 |  | 085113 | d. Will a thermally improved window be required for interior sliding windows? | Thermally improved windows are not required at interior conditions.
113 |  | 085113 | e. page 3, 2.2.H. Does this apply to sliding windows "EE and FF"? | Yes. Provide slide hardware at EE and FF.
114 |  | 085113 | f. Please provide basis of design for sliding window | Provide aluminum assembly similar in appearance and by the same manufacturer as other windows and storefront.
115 |  | 085113 | g. page 3, item 2.3.E. receptor system is noted. Please confirm this is for the head condition only. | Receptor system may not be required. Only provide if deemed necessary by the contractor or fabricator.
116 |  | 085113 | h. page 4 item B at top of page. Please note that storefronts will not be factory glazed. | Noted.
117 |  | 088000 | Regarding section 088000 Glazing. page 2. 2.1.C. Windborne-Debris-Impact Resistant with large and small missile tests are generally for hurricane areas of the country. Please confirm if required. | This requiremnet has been omitted from the spec.
118 |  | 088300 | Section 088300 Mirrors item 2.2D. film backing. Will film backing be required for vertical restroom mirrors set above lav when the mirror is set with mechanical fasteners? | Provide film backing at all mirrors.
119 | A422 |  | A422 shows countertops in the main bathrooms. Please provide a drawings calling out what material these should be and a detail showing how they should be built. | Drawing has been updated to call out Material. SS-1 Solid Surface.
120 |  |  | a. This sheet also calls out countertops for the Conference Room, Breakroom, Training Room and does not specify the material. Can you please specify the material for the countertops (ie. Solid surface or PLAM?) | All countertops shall be Solid Surface.
121 |  |  | Please provide a spec section for damproofing. | Spec section 071113 has been added.
122 | A011 | 133419 | Please clarify required R value for exterior walls. Spec Section 133419 2.2 P calls for R-21 and the drawings (A011) show R-30. Which is correct? | The 2015 Energy Conservation Code for Climate Zone 5 requires the following for metal buildings: Roofs: R-19 + R11 LS (per ASHRAE 90.1), Walls Above Grade: R13 + 13ci., and Walls Below Grade R-7.5ci. Alternatively provide R-30 and achieve a U-Factor of 0.052 as indicated on the drawings.
123 |  |  | The overhead sectional door specs do not refer to the doors having any vision lights. It appears that they doors should have vision lights according to the building elevations. Please provide spec section for vision lights. | Provide manufactures standard insulated vision lights as shown on the building elevations.
124 | A501 |  | Where does 10/A501 occur. It appears that this detail is not needed. Please clarify. | This detail has been removed.
125 |  |  | What floor finish should be applied to the concrete stair in the dispatch? Should there be some sort of stair nosing? Please provide more information. | Provide matching carpet to that used at adjacent floor and ramp. Provide resilient nosing.
126 |  |  | Please specify height of FRP in Janitorial 129 and janitorial/Water 106. | Hight to be 8'-0.
127 |  |  | Please provide spec section for FRP. | 066400 - Plastic Paneling has been provided.
128 | A611 |  | A611 shows sealed concrete in the corridor and other rooms. Please provide spec section for sealed concrete. | Drawings updated to show Polished Concrete in the cooridors.
129 | A611 |  | A611 shows porcelain tile in the bathrooms. There is a spec section for ceramic tile but not porcelain tile. Please clarify which tile is desired. If the tile is to be porcelain can a spec section be provided? | Porcelain Tile has been added to 093013.
130 |  |  | Please provide spec section for CPT-2. | Modular-Walk off by Mohawk added to spec.
131 | A611 |  | The finish plan (3/A611) does not show the temporary walls in the corridor near Janitorial 129. What floor finish should we assume for the temporary corridor? Will the temporary walls need to be painted? Will they need to have rubber base? | The temporary walls should be painted and include base matching the surrounding walls if Alternate 1 is not accepted.
132 |  |  | A roller shade specification has been included in the bidding documents, but I don’t see anywhere on the drawing that calls out which windows are to receive shades. Can a drawing be provided to clarify which window are to receive shades? Should windows coverings be included in the base bid or the alternate? | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
133 |  |  | A fire extinguisher cabinet specification has been included in the bidding documents, please specify where/how many fire extinguisher cabinets will be needed. Will fire extinguishers be needed ion the bus parking area? If so please provide a drawings showing where they will be needed. | Locations of fire extinguishers and cabinets added to sheet A001.
134 |  |  | A building signage spec has been included in the bidding documents. Please provide a drawing or schedule showing which room(s) shall receive signage. | See Spec 101400 3.8 for sign schedule.
135 |  |  | The locker spec calls for 6” legs with closed front end bases, the drawings show a concrete base for the lockers. Please clarify which is correct. | Provide a concrete base as shown in drawings.
136 |  |  | The door schedule hardware sets and door hardware sets in the specification differ as to what doors should receive card readers. Please clarify which shall take precedence, the door schedule or the door hardware sets in the specs. | Provide card readers where shown in communications drawings.
137 | A111 |  | Sheet A111 appears to show a transaction top at the openings ‘EE’. There are no details or sections showing this window sill. Can a detail be provided to show this window sill and show if some sort of transaction surface is required? | Provide a 12" Stainless Steel Counter under the entire length of each EE window with a 12" wide drop-in deal tray in each.
138 |  |  | Do any of the ceilings designated ‘exposed to structure’ require the structure to be painted? | Paint all exposed structure.
139 | A111, A201 |  | A201 Exterior elevations show CMU wainscot veneer that conflicts with the wall types shown on A111. Please clarify which is correct and where CMU wainscot will be needed. | Provide as shown on Exterior Elevations. A111 updated to show Type X1 as intended.
140 |  |  | The enlarged floor plan does not call out wall types for the building areas that are not shown on the enlarged floor plans. Please clarify exterior wall types in the bus parking area 100. Should all exterior walls be ‘X1’ and have drywall? | Exterior walls are 'X1' at the base and 'X2' above. Both are to have 5/8" Gyp on the inside surface as shown on A011.
141 |  |  | Do the retaining walls in the bus parking 100 need a finish (painting? Sealing? Rubbed concrete? or should they be left as exposed concrete with no finish? | Exposed Concrete with no finish.
142 | A111, A423 |  | Please provide section 13/A423. The section cut is shown on A111, but the section is not on sheet A423. | Section 13 "BREAKROOM SECTION" is on sheet A423 (Note: it is out of order and shown above detail 1).
143 |  |  | Wall type A1,A2,B,C,G,H, and J show the wall stopping at the ceiling line. Is this intended to be built to the acoustical ceiling, meaning the ceiling must be installed first and then the wall built to the ceiling? Or should the walls be built 4-6” taller than the ceiling line as they typically are and the ceiling tile/grid laid in after the walls are constructed? | Walls should extend a minimum of 4" above the ceiling. A011 has been updated.
144 |  |  | Please specify distance of sound batt insulation on the ceiling grid from the wall. | The insulation has been removed.
145 | A423 |  | The plastic laminate base and uppers cabinets are on details 2 and 4 on A423 are not specified, should these match the breakroom (PL-1)? | To be selected by Owner and/or Architect from full line.
146 |  |  | The specifications for SS-1 and PL-1 (solid surface and plastic laminate) call out manufactures but do not specify a color/texture. Can a specific material spec be provided, or can a material allowance be specified? | To be selected by Owner and/or Architect from full line.
147 | A501, A502 |  | Details 9/A501 and 9/A502 appear to show a steel angle and a steel wide flange beam. Neither of these items are on the structural framing drawings. Would it be acceptable for these items to be engineering and provided as part of the pre- engineered metal building? If these are to be steel structure, can a drawing be provided showing how/where they are supported and connection details | These items should be provided as part of the pre-engineered building structure
148 |  |  | Can you please clarify who will be paying for tap fees? | Contractor.
149 |  |  | Can you please clarify if the new 2” gas line is to be by the GC or by CSU? | CSU up to and including meter. Contractor on facility side of meter.
150 |  |  | Can you please provide a soils report or specify and assumed bedrock depth so that all contractors are bidding the same depth? | The Geotechnical Engineering Report is contained in Appendix A of the Project Manual (Volume 2), following Section 334200 Stormwater Conveyance. A bid depth of 45' should be used.
151 |  | 011000 | Spec section 011000 1.6 B 1 states that A/V and IT is to be by the owner and telecommunication drawings were included as part of the bid set. Can you please clarify what AV/IT will be by owner and what AV/IT will be by the GC? | 011000 is intended to refer only to items "designated to be by owner". Such instances are noted in the drawings. Itmes not designated as such are by the GC. Refer to Communications Responsibility Matrix on drawing Sheet T003 for Contractor/Owner requirement.
152 | T111 |  | T26/T111 shows data for future charging stations. Is this data intended to be run in conduit below the slab? Or is it intended to be dropped down form the building structure, if the latter is the case how should the conduit be supported? | These are ceiling mounted data drops to be dropped down in the future. At this time, the data shall be terminated at a celing enclosure.
153 | T111 |  | 2/T111 shows pendant speakers in the Corridor A 131A. is the intent to have pendant speakers in this hallway with acoustical grid and tile? | The "P" in the drawings designates public address speaker, not pendant. Provide 2x2 layin speakers for ACT locations.
154 |  |  | What is the thickness, base course requirement and reinforcing requirement of the exterior slab between the building and the retaining wall along grid line 14? | 4-inch concrete with No. 4 Rebar at 18" o.c. each way. Typical section has been provided on Sheet C104
155 | S502 |  | Can you please identify where detail 7/S502 is required? | This detail is for any areas where the slab is not poured continuously and a construction joint is needed
156 |  |  | Should the stairs in the driver dispatch room have reinforcing or dowels in the slab? If so, please provide a detail/drawing. | Provide at conctractor discresion.
157 | S500 |  | Please specify depth and width of footing in details 1,2,4/S500 | The pier cap schedule is located on sheet S101, and provides the sizing
158 |  |  | Can a detail for light pole bases be provided? | The detail for the light pole base in on Sheet E502.
159 | P100 |  | Note P1 on P100 says that the architect will provide the trench drains. Please confirm that the GC is not responsible to include costs for the trench drains. Can a spec be provided so that we know what we need to install? | Contractor to include cost for trench drain assembly. Trench drain model provided on updated drawings, as part of keynote P1.
160 | P111 |  | P111 shows multiple hose bibs in the bus parking area. How should the hose bibs be secured since they are not on a wall or a column? Can a detail be provided to show how they should be secured? | Hose bibbs to be secured to the wall using verticle clamps as specified in Spec section 220529. Hose bibb locations moved to walls, refer to revised drawings.
161 |  |  | The mop service basin remarks says to provide ‘S.S wall guards. The architectural drawings indicate that FRP is be installed on the walls. Please clarify which is correct. | S.S. wall guards to be provided for the mop service basin. Additional FRP to be installed as called for by the architect.
162 | P301 |  | 1/P301 shows (2) hose bibs to be installed as part of the alternate 1 buildout. Should these be part of the base bid if the exterior walls are to be finished and to limit the amount of cutting exterior CMU to add hose bibs? | Hose bibbs to be installed as part of base bid.
163 | M105 |  | 3/M105 references insulation. Can a spec be provided for the insulation and can you verify where the insulation should be applied? | Spec 232113 - Hydronic Piping has been updated to include a section specific to the snowmelt tubing and installation. This section provides information on the underslab insulation and edge insulation. Drawing M105 has been updated to include a note clarifying where insulation should be applied and what size and type of insulation to be used
164 | G000 | 011000, Request for Proposal | Specification 011000 part 1.4B and plans list Mountain Metropolitan Transit as the Owner. The RFP lists the City of Colorado Springs as the Owner. Please clarify how the Owner will be listed on the contract: The City of Colorado Springs or MMT? | The City of Colorado Springs.
165 |  |  | Can you please issue a bid bond form? | Word Documents were uploaded into Bidnet for easy input. (Also - please see Addendum 2 Form, question 5.)
166 |  | Request for Proposal Section IV | Section IV Special Contract Terms and Conditions lists construction wage rate requirements. Can we please get a copy of the Davis Bacon/Prevailing wage schedule if this is required? | Please see Addendum 2 Form, question 6.
167 |  | Request for Proposal Exhibit 4 | Exhibit 4 (Minimum Insurance Requirements) has some contradictions regarding Professional Liability Insurance coverage requirements. Page 76 lists the required limit is $2M occurrence/$2M aggregate. Page 78 lists that the limit required is $1M occurrence/$2M aggregate. Please clarify Professional Liability Insurance coverage requirements. | Please see Addendum 2 Form, question 7.
168 | S103 | 079200 | Control joint plan S103 does not call for each control joint to be filled with joint sealant. Spec section 079200, 3.4, C calls for joint sealant in isolation joints in concrete slabs. Does this include all control joints at the interior slab, or only edge joints? Please clarify. | All control joints shall be filled
169 | A114 |  | Please clarify locations of window treatments. | All windows in the Admin Area are to receive window treatments.
170 | A114, E211B | 122413 | Specification 122413 (Roller Shades) part 1.1 A1 indicates manual shades but parts 1.2 B and 3.1B indicate motorized shades. Please clarify which is correct, manual or motorized shades. If motorized, please add power to electrical plans. | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
171 |  | 122413 | Specification 122413 (Roller Shades) part 2.2 G list all the options for shades. Please verify fascia, headbox or recessed pocket. | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
172 |  | 122413 | Specification 122413 (Roller Shades) part 2.4 C 2 mentions skylights; we did not see any in the plans, please confirm these are not required. | Spec 122413 has been deleted. There are no skylights in the project.
173 |  | 122413 | Specification 122413 (Roller Shades) part 3.1 A 1 asks for opaque but part 2.1 F 1 says light filtering. Please confirm which is correct, blackout or light filtering. If light filtering what openness? | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
174 | L101, L102 |  | Landscape sheet L101 depicts a different quantity of plants than the plant schedule on sheet L102. See counts below. Shrubs/Ground Cover per plan vs. schedule -MAQ (32 vs 34 each) -MRE (12 vs 17 each) -PBE (24 vs 20 each) -PCI (9 vs 8 each) -RTI (12 vs 14 each) Please clarify which is correct, plan or schedule. | Quantities should be: (32) MAQ (12) MRE (24) PBE (8) PCI (12) RTI
175 |  |  | The RFP states that the proposal due date is 12/11/20 while the award of contract date will be May of 2021. Is this correct? The spread between these dates will make cost containment of our subcontractors materials and labor prices difficult if not impossible. Please advise | Please see Addendum 2 Form, question 1.
176 |  |  | What is the anticipated Budget for this project? | Please see Addendum 2 Form, question 2.
177 |  |  | There are no pier lengths, top of pier cap elevations or top of wall elevation on the structural drawings, will these be provided to know lengths of piles etc.? | The pier cap schedule is located on sheet S101, and provides the sizing
178 |  |  | Is it the intent of the Design team and the City to have the metal building be a D/B including the structural drawings or will the Design Team prepare final Structural Drawings once the Metal Building is designed? | The PEMP will be delegated design and fully engineered by the PEMB Manufacturer.
179 |  |  | The RFP states that the Contractor must hold their pricing for 90 days after submission. The selection of the RFP is rough 139 days after submission. Please advise on this discrepancy. | Please see Addendum 2 Form, question 3.
180 |  |  | Please clarify how the Owner will be listed on the contract: The City of Colorado Springs or MMT? | Please see Addendum 2 Form, question 4.
181 |  |  | Can you please issue a bid bond form? | Word Documents were uploaded into Bidnet for easy input. (Also - please see Addendum 2 Form, question 5.)
182 |  |  | Would it be possible to extend the question deadline through Nov 18, 2020. | Please see Addendum 2 Form, questions 8 and 19.
183 |  |  | Confirm the Davis Bacon wage determination number C020200022 dated 10/30/2020 is the correct pay scale to use on this project. | Please see Addendum 2 Form, question 9.
184 |  |  | With contract award occurring in May 2021, will the successful contractor receive a Letter of Intent shortly after submitting our proposal, such that we can secure pricing with selected subcontractors. Holding subcontractor pricing beyond 30 days is difficult let alone nearly five month. | Please see Addendum 2 Form, question 10.
185 |  |  | Please provide the geotechnical engineering prepared by Terracon referenced in spec section 011000 | Please see Addendum 2 Form, question 11.
186 | A011 |  | Sheet A11 general note 2 calls for Room 111A to have a raised floor system. Please provide a specification for this system. | See Drawing 3/A401.
187 | A611 |  | Sheet A611 specifies Room 111A is to receive CPT-1. Confirm this is compatible with raise floor system | Confirmed.
188 | A611 |  | Polish concrete is more expensive than sealed concrete. Please confirm the rooms that are scheduled to receive the polish concrete (PC) as noted on sheet A611. | The Room Finish Schedule has been updated.
189 |  |  | Will there be liquidated damages associated with this project? | Please see Addendum 2 Form, question 12.
190 |  |  | Please confirm a bid bond will be required in the proposal. | Please see Addendum 2 Form, question 13.
191 |  |  | Please confirm a P&P bond will be required. | Please see Addendum 2 Form, question 14.
192 |  | 230923 | What is the process to gain approval to submit a proposal to the contractors for the DDC system? Setpoint Systems meets the system description described in section 230923-6, and would like to compete. This would be in part 2.1.B on that page. | Systems that meet the requirements of the specifications may be submitted to the engineer of record for review. If the system meets all requirements then it will be approved as an equal to the listed manufacturers.
193 |  |  | With the project not being awarded until Approximately May of 2021. How should the contractor handle escalation of material pricing? With the election still in limbo there are many market sectors that will be reporting pricing escalations at some point. Will this be handled at time of award of contract? Or will there be an escalation clause in the contract? | Please see Addendum 2 Form, question 15.
194 |  |  | With the last day for questions being today at 10:00 AM, how do we handle questions that may arise with the building department reviews and subsequent redistribution of plans? | Please see Addendum 2 Form, question 16.
195 |  |  | What is the sales tax rate we are to use for this project? What is the use tax rate we are to use for this project? | Please see Addendum 2 Form, question 17.
196 |  |  | Please confirm that Enclosures 1A, 1B, 2, 3 and 4 (DBE documents) of the RFP must be submitted with the proposal. | Please see Addendum 2 Form, question 18.
197 |  |  | Please confirm that Lu-Tek is an acceptable manufacturer for manual roller shades. Substitution request submitted to Andrea Davenport. | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
198 |  | 011000, Request for Proposal | Specification 011000 part 1.4B and plans list Mountain Metropolitan Transit as the Owner. The RFP lists the City of Colorado Springs as the Owner. Please clarify how the Owner will be listed on the contract: The City of Colorado Springs or MMT? | The City of Colorado Springs
199 | S103 | 79200 | Control joint plan S103 does not call for each control joint to be filled with joint sealant. Spec section 079200, 3.4, C calls for joint sealant in isolation joints in concrete slabs. Does this include all control joints at the interior slab, or only edge joints? Please clarify. | All control joints shall be filled
200 |  |  | Please clarify locations of window treatments. | All windows in the Admin Area are to receive window treatments.
201 |  | 122413 | Specification 122413 (Roller Shades) part 1.1 A1 indicates manual shades but parts 1.2 B and 3.1B indicate motorized shades. Please clarify which is correct, manual or motorized shades. If motorized, please add power to electrical plans. | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
202 |  | 122413 | Specification 122413 (Roller Shades) part 2.2 G list all the options for shades. Please verify fascia, headbox or recessed pocket. | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
203 |  | 122413 | Specification 122413 (Roller Shades) part 2.4 C 2 mentions skylights; we did not see any in the plans, please confirm these are not required. | Spec 122413 has been deleted. There are no skylights in the project.
204 |  | 122413 | Specification 122413 (Roller Shades) part 3.1 A 1 asks for opaque but part 2.1 F 1 says light filtering. Please confirm which is correct, blackout or light filtering. If light filtering what openness? | Spec 122413 has been deleted. The owner has opted for metal louver mini-blinds to be installed at all windows in lieu of roller shades. Contractor furnished and installed as part of Admin Alternate.
205 | L101, L102 | L101, L102 | Landscape sheet L101 depicts a different quantity of plants than the plant schedule on sheet L102. See counts below. Shrubs/Ground Cover per plan vs. schedule -MAQ (32 vs 34 each) -MRE (12 vs 17 each) -PBE (24 vs 20 each) -PCI (9 vs 8 each) -RTI (12 vs 14 each) Please clarify which is correct, plan or schedule. | Quantities should be: (32) MAQ (12) MRE (24) PBE (8) PCI (12) RTI
206 |  |  | Is there a required bid bond form for this project? We could not find it in the bid documents. | Please see Addendum 2 Form, question 20.
207 |  |  | This section states the city will employ and pat for services of an approved testing laboratory to perform specified services for the field testing. The next paragraph state the contractor shall perform, or arrange for the performance, and pay all costs in connection therewith, all other tests and inspections required by the contract documents. What testing will be paid by the city and what testing will be paid by the contractor? | The City will contract with a 3rd party for the purpose of Quality Assurance (or Verification) testing for: Soil Compaction Control; Cast-in-Place Concrete; and Asphalt Concrete Pavement. The Contractor is responsible for the performance and associated costs for all other tests and inspections required by the contract documents and for any Quality Control testing that the Contractor deems necessary to ensure conformance of proposed materials and installation with project requirements.
208 | A001, A011 | 133419 | I have a question regarding the desired insulation. There are a few different options based on the plans vs the specs which would change the cost considerably. In the specs page 446 (133419-5) notes insulation in the roof is R-38 (double insulation layer with thermal blocks) and the walls are R-21. Then, in the architectural drawings A001 (pg 64) it states the roof is R-19 + R-11LS and the walls are R-13 + R-13ci. Then in the architectural drawings A011 (pg 68) wall assembly detail page it states the walls as R-30. Please advise which method is preferred. | The 2015 Energy Conservation Code for Climate Zone 5 requires the following for metal buildings: Roofs: R-19 + R11 LS (per ASHRAE 90.1), Walls Above Grade: R13 + 13ci., and Walls Below Grade R-7.5ci. Alternatively provide R-30 and achieve a U-Factor of 0.052 as indicated on the drawings.
209 |  |  | Should we be working off of plans “2020-10-29 MMT Campus Expansion - 100% CD For Bid – Drawings” or “2020-10-29 MMT Campus Expansion - 100_ CD For Bid – Drawings”? | All current drawings are included in Addendum 2.
210 |  | 093013 | I see that there is an accent wall tile spec provided in the ceramic tiling specification 093013 – 2. However, I do not see where the accent tile is to be used on the plans. Can you please provide a scope for the accent tile. | No accent wall tile is included in the drawings.
211 |  |  | Should we include waterproofing membrane at the floor tile? | The floor tile requires a crack isolation membrane, reference specification. The wall tile will not need a waterproof membrane.
212 |  |  | Should we include waterproofing membrane at the wall tile? | No
213 |  |  | In the restrooms, there is a wall separating the sinks with the toilets…should we include tile on the end of that wall? | Yes. Provide tile consitently on all walls in the restrooms.
214 |  |  | The specification for the floor tile in the restroom is rated for wall tile only…Would the architect have a different material they would like to use for the restroom floor tile or should we use an allowance at this time? | Precelain floor tile added to 093013.
215 |  |  | What product is to be used for CPT2 in the Vestibules? | Modular-Walk off by Mohawk added to spec.
216 |  |  | Should we include moisture testing? | If required by specifications.
217 |  |  | Should we include tile at the drinking fountains? | No
218 | A011, A102, A111 |  | Roof assembly R1 on sheet A011 indicates a metal liner panel finish. However, detail 1 on sheets A102 and A111 indicates the ceiling is exposed to structure. Please clarify what the intent of the finished ceiling will be (exposed to structure or interior ceiling liner) | Metal Liner Panel.
219 |  |  | There are numerous trades that are required for this project that are not listed on the provided prevailing wage sheet. Please advise how to classify the trades that are not listed. | Please see Addendum 2 Form, question 21.
220 |  | 230923 | Would the City of Colorado Springs please consider adding Johnson Controls Inc. as an equal Manufacturer of Direct Digital Controls in section 230923.2.1? | Yes, Specification has been updated accordingly
221 |  | 233600 | Would the City of Colorado Springs please add Johnson Controls as an equal Terminal Manufacturer to section 233600.2.2.A? | Yes, Specification has been updated accordingly
222 |  | 237416 | Would the City of Colorado Springs please add Johnson Controls as an equal Rooftop Air-Conditioning Manufacturer to section 237416.2.2.A? | Yes, Specification has been updated accordingly
223 |  | 238126 | Would the City of Colorado Springs please add Johnson Controls as an equal Split System Air-Conditioning Manufacturer to section 238126.2.1.A? | Yes, Specification has been updated accordingly
224 |  | 101400 | Please provide a sign schedule showing types and quantities of all signage required. | See Spec 101400 3.8 for sign schedule.
225 | A611 | 099123, 033543 | What product type is desired for sealed concrete floor finishes? Interior Paint Specification lists a Water Based Concrete Floor Sealer System and a Clear Polyaspartic Sealer with no deviation as to which sealer is to be used. 03 35 43 Polished Concrete Finishing Specification lists an Ashford penetrating sealer, but it cannot be determined if this product is only applicable at areas to receive Polished Concrete. | Ashford penetrating sealer intended for use in areas with polished concrete.
226 |  |  | Please provide a matrix of the charging infrastructure & equipment that is to be provided under a future, separate contract. There appears to be confusion amongst the electrical contractors as to what is to be provided as part of the base bid. | The drawings show four chargers that will be initially installed but under separate contract. The electrical contractor is to provide infrastructure up to and including the electrical disconnects for that equipment. Conduit to the future utility transformer is to be installed as noted on the site drawing.
227 | A001 |  | Wall assembly X1 shows 5/8" Exterior Sheathing at 4" Concrete Masonry Units. What material is to be used at these locations? (OSB, Gyp Sheathing, Plywood, etc. ) | Gyp. Sheathing
228 |  | 83613 | Please confirm that all sectional and overhead doors will be motorized. Specification speaks to both manual and electric door operators, and door schedule does not designate. | Motorized.
229 | A601 |  | Please provide a specification or product information for door type G. (12'X14' Bi-Fold Hollow Metal Door). | Specification 083513 - Folding Doors has been added.
230 | A601 |  | Opening 132 Trash Enclosure schedules a "type G door". This appears to be incorrect, and should read "Type F" for the trash enclosure gates. Please clarify. | Type F is correct. The schedule has been updated.
231 |  |  | Please specify a walk-off carpet (CPT-2) for use at entry doors. | Modular-Walk off by Mohawk added to spec.
232 |  |  | Please specify a porcelain floor tile for use in the restrooms. The project manual calls for “CT-2 Daltile Dimension” – it is assumed to mean Daltile Modern Dimension, which is ceramic product and not rated for use at floors. | Specification Section 093013 updated to include porcelain tile flooring.
233 |  |  | Plans call for Schluter to terminate ceramic tile in the restrooms, while the project manual calls for bullnose; please clarify which is desired. | Schluter
234 |  | 133419 | Will alternate metal building manufacturers be considered or is A&S Building System to be the sole-source provider? | Open to all manufacturers meeting the specifications.
235 |  | 133419 | Metal Building System spec section calls out for fiber-cement siding and soffit. Where do these conditions exist? | There is no fiber-cement siding and soffit. Specification has been updated.
236 |  | 074113.16-1 & 074213.13-1 | Are PEMB manufacturers required to use the Berridge products specified or will alternate products, that are equivalent to the specification be permitted? | Open to alternate products meeting the specifications.
237 |  | 133419 | Spec section references a metal building product that is a division of NCI. NCI (now Cornerstone Building Brands) represents 7+ metal building systems. Are any of these systems an acceptable product for bid purposes? | Open to all manufacturers meeting the specifications.
238 |  | 133419 | Spec section states that metal building systems shall withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated according to procedures in MBMA's "Metal Building Systems Manual" and then goes on the state that design loads are as "indicated on drawings". The drawings do not appear to provide design loads. Please advise as to what shall be assumed for bid purposes. | A separate fully engineered plan set specific to the metal building shall be provided by the manufacturer.
239 |  | 64116 | Spec section states AWI certification labels and certificates will be required for the project, and that fabricators and installers must be a licensed participant in AWI's Quality certification program. In an effort to obtain the most competitive pricing, may this requirement be waived if plastic laminate clad architectural cabinets are built to AWI standards? | AWI's Quality certification may be waived if built to AWI standards.
240 |  | 93013 | Spec sections notes an accent wall tile. Where does the accent wall tile occur? | No accent wall tile is required.
241 |  | 93013 | Does wall and/or floor tile require a waterproof membrane? | The floor tile requires a crack isolation membrane, reference specification. The wall tile will not need a waterproof membrane.
242 |  | 93013 | Does the wall separating the sinks with the toilets receive wall tile? | Yes.
243 |  | 93013 | Is tile required at wall behind water fountain? | No
244 |  | 315000 | Can design team elaborate on what they believe will be required of this spec section? The civil documents do not appear to reference any shoring. Grade lines suggest that temporary shoring of the NE corner of the site may be required while constructing the cast-in-place retaining wall. Is this the intent of the design team? | Permanent or Temporary shoring required for construction shall be based on the contractor's means and methods. If the contractor determines that shoring is needed, they will need to submit a stamped shoring design for review by the structural engineer per the specifications.
245 |  | Terracon GeoReport | Soils report recommends gravel under slab with a vapor barrier, but neither structural nor architectural drawings reference this recommendation. Please advise whether or not gravel & vapor barrier are required beneath the building slab. If yes, please provide depth/size of gravel and thickness of vapor barrier to be included in base bid. | Provide a vapor barrier as required by the Geotech Report. Provide a minimum of 4" gravel or as otherwise specified.
246 | Pg 11 | Terracon GeoReport | Geotech report recommends that the detention basin be lined with a minimum 2-foot thick layer of compacted clay soils or a relatively impervious man-made product, such as an HDPE liner, for additional slope protection. There does not appear to be any mention of this in the Contract Documents. Please advise as to whether or not this recommendation needs to be priced as part of the base bid scope of work. | Yes, this recommendation needs to be priced. Typical Cross Section of has been added to Sheet C312 referencing 2' of clay liner within the detention pond. Refer to revised Specification 312000, Part 2, 2.1(I).
247 |  | 83613 | Please confirm that the 10 year special warranty for materials, workmanship, and finishes for sectional doors are applicable to this project. | Yes.
248 |  | 133419 | The plans clearly say that the building is to comply with 2015 IECC energy code climate zone 5 and call out the U-Value requirements for the envelope on sheet A001. But the specification in division 13 calls out a different insulation R-value and a different installation method. (referencing Division 13. page 133419 - 3, Part 2 -PRODUCTS, 2.2 PERFORMANCE REQUIREMENTS) And the installation or execution sated below. (referencing PART 3 - EXECUTION on page 133419 – 11, 3.5 THERMAL INSULATION INSTALLATION) The specification shown here is specifying different insulation and methods of execution that are not the same as the plans have. Question is if the roof insulation is to meet the minimum of 2015 IECC energy code of U factor of 0.035 or a different U factor such as 0.031 or 0.029 ? | The 2015 Energy Conservation Code for Climate Zone 5 requires the following for metal buildings: Roofs: R-19 + R11 LS (per ASHRAE 90.1), Walls Above Grade: R13 + 13ci., and Walls Below Grade R-7.5ci. Alternatively provide R-30 and achieve a U-Factor of 0.052 as indicated on the drawings.
249 |  | 133419 | Is the wall insulation to meet the minimum of 2015 IECC energy code of U factor of 0.052 ? | Correct.
250 |  | 133419 | Can any method of fiberglass insulation installation be used as long as the U factor can be backed up from testing or modeling ? | Yes.
251 | A611 |  | Please confirm the rooms that are scheduled to receive the polish concrete (PC) and sealed concrete (SC) as noted on sheet A611. Example is JAN room 129 is noted as PC, whereas Corridor 131A is noted as SC. | The room schedule has been corrected.
252 |  |  | Provide a specification for CPT-2 (walk-off mats) and PT (porcelain tile). | Modular-Walk off by Mohawk added to spec.
253 |  |  | Please provide required bid bond form and clarify the bid bond amount as referred to under Exhibit 11 "Bonding Requirements" | Please see Bonding Word Documents added
254 |  |  | Please provide a specification for rough carpentry | Specification 061000 Rough Carpentry has been provided.
255 |  |  | Please provide specifications for water and sanitary utility systems | Specifications for exterior water and sanitary shall be in accordance with Colorado Springs Utilities Line Extension and Service Standards ( WaterLESS and WastewaterLESS)
256 | T111 |  | For WAPs noted as T36 on sheet T111, please confirm cable only scope with jacks on both ends. | One side needs to be punched down on the patch panels and the other side (at the AP) needs to be terminated on a biscuit jack. As note T36 indicates, rough-in includes cabling - connectorized on both ends and tested.
257 |  |  | Please confirm whether Structured cabling contractor will be responsible for providing all IDF and MDF equipment, Racks, cable tray, and cable management, or if Owner will provide. | Refer to the Responsibility Matrix on Sheet T003 and Telecom Equipment Schedules on Sheet T005 for listed responsibilities as well as equipment to be provided by the contractor. The owner will only be responsible for providing electronic equipment (servers, switches, UPS, etc.).
258 | A011 |  | Wall type "F" shows a "Rated Expansion Filler (UL-HW-D-0113 & HW-D-0115). Is this intended to be mineral wool, or a fire rated expansion joint that runs full length of rated CMU wall that demises administration area from bus parking? | Intent is to provide a continuous 2 hour separation between the Admin area and the bus garage.
259 | A111 |  | Please confirm that the wall along GL3 is the Type F masonry wall as no wall tag shows on the plan. Also, does the masonry wall continue on an angle at Storage 121? | Correct. Please see wall Tags on A111.
260 | A201 |  | Where/how does the CMU wainscot terminate on the east elevation of the building? In elevation, it appears the concrete ramp is directly adjacent to the building, but in section it shows the CMU wainscot. Please provide a GL to terminate CMU wainscot as well as a termination detail if it does die into the concrete ramp. | Wainscot continous all the way around the East side of the building and through the mechanical yard.
261 |  | 323119 | Spec section 323119 1.3 C calls for a crash rated fence system. The "ornamental fence illustration" on sheet C104 shows a non-crash rated "typical iron fence." Please advise if a crash rated fence system is required. | No, a crash rated fence system is not required.
262 |  |  | Should bidders assume any framing and/or gypsum board at the interior side of the exterior walls in the admin buildout area to be part of the base bid or will all framing & drywall of exterior walls be part of the Alternate? | Part of the Alternate.