## Table 1
Steve, Larry, Tim | [6 empty] | Q & A for Addendum #3
Andrea (Larry, Tim, Doug)
SEH (w/ minor input from Lollar)
AS OF: | 2020-11-19 | 11:40
Contractor and Contractor's RFI # | Scope of Work (Category) | or Lollar | (or sub) | Question Number | Drawing Sheet Number | Specification Number | Question | Response
W.E. O'Neil #1 |  |  | X | 1 - 262 | These questions were in Addendum #2
|  |  |  | 263 |  | 083613 | Safety bottom sensing edges, photo eyes or both? The specifications list both. With safety bottom edges, the door would have to actually make contact with something or someone for it to reverse. With safety photo eyes, the door reverses without making contact. | Provide both bottom sensing edges and photo eyes as stated in the specifications.
|  |  |  | 264 | 9/A501 | 083613 | Standard lift or High Lift track Overhead Door Operators? The documents call for standard lift. | Specification Section 083613 and drawing detail 9/A501 should be revised to provide wall mounted Heavy Duty High Lift Track Overhead Door Operators.
|  |  |  | 265 |  |  | Substitution request for: DDC Controls | Addressed in Addendum 2.
|  |  |  | 266 |  | 087100 | Substitution request for: Door Hardware May the following be submitted in lieu of the specified products? - Dorma Auto Opener ED 900 - Stanley Precision PHI APEX 2000 Heavy Duty Exit Device - Stanley Commercial Door Closer QDC-100 | The Dorma Auto Operator ED 900 and the Apex 2000 Exit Device appear to be acceptable substitutions. It is unclear if the Stanley Commercial Door Closer QDC-100 is an equal product as insufficient information was provided.
|  |  |  | 267 |  | 105113 | Substitution request for: Lockers HPDE Lockers in lieu of metal lockers? | HPDE Lockers will be considered an acceptable substitution for metal lockers provided that all performance criteria of the specifications are met. They must be cleanable, lockable, have metal hardware and number plates on the outside for assignment purposes. The lockers must also have a mail slot as described in the specifications.
|  |  |  | 268 |  | 133419 | Substitution request for: PEMB | Addressed in Addendum 2.
|  |  |  | 269 |  |  | Substitution request for: Cast Stone in Lieu of Precast | Cast Stone will be considered and acceptable substitution for precast provided that all performance criteria of the specifications are met.
|  |  |  | 270 |  | 122413 | Substitution request for: Roller Shades | Addressed in Addendum 2. Roller shades have been removed form the project. Metal louver mini-blinds are to be provided at all locations. Owner intent is to provide a product similar to that used in other buildings on campus.
|  |  |  | 271 |  |  | Substitution request for: Snowmelt Will the Reillo Condexa 399 boiler be accepted as a substitution for the specified product. | The Reillo Condexa 399 boiler appears to be an acceptable substitution.
|  |  |  | 272 |  | 033000 | Substitution request for: Vapor Barrer Systems | All submitted products fully meeting the specifications as written will be considered.
|  |  |  | 273 |  |  | Sight and Sound Technologies requested to be added as a qualified contractor for A/V. | A condition of pre-qualification is that the contractor must have a qualified programmer on staff rather than utilizing a contracted programmer.
|  |  |  | 274 |  |  | QComm requested to be added as a qualified contractor for A/V. | Qcomm will be considered as a pre-qualified A/V contractor under the condition they can submit or confirm they are CommScope Uniprise Structured Cabling Certified as specified.
|  |  |  | 275 |  | 012900 | Question about order of precedence in the contract documents. | Section 012900, 1.2.B.1 shall be updated to read: "City of Colorado Springs “Schedule B - General Construction Terms and Conditions” posted on the City’s website at https://coloradosprings.gov/procurement-services/page/procurement-regulations-and-documents?mlid=10046), for the latest version of the City of Colorado Springs Procurement Rules, Regulations, and Information. NOTE: in case of discrepancy between the City of Colorado Springs “General Construction Terms and Conditions” and the Project Manual, the city “General Construction Terms and Conditions” shall take precedence."
|  |  |  | 276 |  | 087100 | Allegion submitted a substitution request form to provide equal door hardware products to those listed in the specifications. | Full hardware specifications prepared and provided by Allegion and meeting the current specifications using products deemed equal will be accepted.
|  |  |  | 277 |  |  | Addenda #02 states the GC is responsible for permit fees & tap fees? Typically the tap fee is part of the initial development fees. Can you confirm that we are to carry those costs and which department shall we contact for pricing as we cannot seem to locate a tap fee schedule on the ColoradoSpring.gov website. Addenda #02 states that the City has already paid the plan review fees, so in order to calculate the permit fees via the Pikes Peak Regional District calculator, we would need the Architect to provide: Construction Type (1A, 1B, etc) and Occupancy Type | (Refer also to Question 148 in the Addendum 2 spreadsheet) The Contractor is responsible for both Permit Fees and Tap Fees. The Construction Type is II-B as indicated on drawing sheet A001. The Occupancy Types are Group B and Group S-2 as indicated on drawing sheet A001. Bidders are referred to the Colorado Springs Utilities (CSU) “2020 Development Charges and Fees” information sheet (https://www.csu.org/Documents/DevelopmentCharges.pdf). Note the fees shown are for non-commercial development and may be different for the Campus Expansion Project. Bidders should contact Customer Contract Administration for assistance in determining the tap fees.